## Slide 1
HPS TechSupport: Center of Excellence
Experion Site Network Audit report

## Slide 2
Network Audit report | HPS LSS GTAC
SF- 199862 | SR 1-18568222761(Network Analysis - Experion Migration: R400.2 to R500.2)
Chart: 
| Poor | Caution | Healthy
Column1 | 0 | 37 | 37 | 26 | 100
Chart: 
| GV | GV+ | END
Indicator | 150 | 20 | 800
NETWORK AUDIT SUMMARY
Compatibility | Running Config | Interface Status | CPU Utilization
Switch Model | Uplink Port | Interface Errors | Avg/60 secs
IOS Version | L1 Port | Switch Logs | Avg/60 Mins
 | L2 Port | Spanning Tree | Avg/72 hrs
Severity | OBSERVATIONS | RECOMMENDATIONS
 | The Switches are not configured with Honeywell latest switch configuration template. There are missing configurations with respect to Access Control List, storm control and QOS settings etc. in the switches. | Reconfigure the switches with Honeywell's latest switch configuration files & ensure that the missing configuration with ACLs ,storm control and QOS are in place to comply with FTE configurations.
 | Honeywell qualified switches are used, but the IOS version of switches is not latest/recommended one | It is recommended to update the switches with latest Honeywell supported IOS. Refer the attached PDF document for qualified IOS in Appendix – C section
GENERAL INFORMATION
Customer | Evonik Cyro LLC - Osceola
Experion Release : | R400.2
Audit Report Date: | 10/30/2017
Site Contact : | William Bauer
Prepared By | HPS Technical Support
L1/L2 FTE Switch
Node
Overall Network Status
FTE Checker | Domain Control | FTE Auxiliary
NIC Setting | Host File | FTE Status Display
FTE/System Management version | Reverse Lookup Zone Painter | FTE/Non FTE Node List
Embedded node | Windows Events Logs | 

## Slide 3
Network Audit report | HPS LSS GTAC
SF- 199862 | SR 1-18568222761(Network Analysis - Experion Migration: R400.2 to R500.2)
Severity | OBSERVATIONS | RECOMMENDATIONS
 | CRC errors are observed on the switches ports | Ensure that there is no speed/duplex configuration mismatch or media converter problem on the end device connected
 | Multicast storm detected on ports of few switches | Ensure that the FTE multicast & SRP multicast address is different in the FTE cluster.
 | Frequent mac flap observed on few of the switch ports | This is an indication of wrong cable/connection/FTE binding. Verify cable connections are proper meaning Yellow adapter to Yellow switch and green adapter to green switch. Perform crossover cable removal test and ensure A > A and B > B are showing OK and remaining showing silent.
 | Spanning tree priority is not configured properly for top level switch. Hence the root bridge calculation is not correct. As per Honeywell recommendation, the FTE switches must configure with spanning tree priorities for mst0 instance. No other configurations are supported or qualified by Honeywell. Note: You are having only pair of switches in the Network and are configured as split switches, it is OK to add the spanning tree priority. But it is not recommended to configure split switches as top level switches and the spanning tree priority on the switches. In future if you are adding more switches, then make sure that the spanning tree priority is configured on top level switches and the top level switches are not split switches. | As per Honeywell recommendation, the top level FTE switches must configure with spanning tree priorities for future expansion point of view. Hence configure spanning tree priority as 4096 on top level Yellow switch and 8192 for Green switch. It is very important to note that the spanning tree re configuration may cause LOC/LOV on running plant. Hence execute these commands in a controlled manner. Add the following commands in to Global switch configuration of top level yellow switch spanning-tree mst 0 priority 4096 and in top level green switch: spanning-tree mst 0 priority 8192

## Slide 4
Network Audit report | HPS LSS GTAC
SF- 199862 | SR 1-18568222761(Network Analysis - Experion Migration: R400.2 to R500.2)
Severity | OBSERVATIONS | RECOMMENDATIONS
 | Follow the mentioned checklist for EHPM/EUCN integration | Please see Appendix in Chapter 6 for this checklist items in the attached document:
 | If using the router in the network: Ensure that router port , which is connected to the L2 switch must configure with the below commands : no ip redirects no ip unreachables no ip proxy-arp no ip mroute-cache | 
 | Refer the attached Excel sheet from Appendix – C “Switch DataAnalysis_199862.xlsx” for further details | 
 | Discrepancies are observed in NIC settings configurations on FTE Nodes. Refer attached Excel sheet from Appendix – C “FTE Checker output Analysis_199862.xlsx” for further details | 
 | Honeywell recommendation is not to configure hosts file in DC for any hosts which are already part of the DNS server. Refer the section Number 23,27,28 & 29 of attached “TAC_Experion_Audit_Network_rev13.pdf” about DC related configurations. | 

## Slide 5
Network Audit report | HPS LSS GTAC
SF- 199862 | SR 1-18568222761(Network Analysis - Experion Migration: R400.2 to R500.2)
Appendix A – Glossary of Terms | 
FTE | Fault Tolerant Ethernet
NIC | Network Interface Card
 | Status is good – no issues or recommendations
 | Status is bad – This condition needs immediate attention. See the recommendations.
 | Status is marginal –Warning/ Not compliance with latest best practice. See the recommendations.
 | Information, observations, and recommendations
 | Color indication in the Network status
 | Configuration is OK configurations is not OK, correction required Configuration is not supported need immediate attention No data available, not analyzed
Appendix B – Analyzed Devices | 
Cisco switches "Yellow_Split_Switch" "Green_Split_Switch" | Model WS-C2960-24TT-L WS-C2960-24TT-L
FTE checker Output | 
Appendix – C Attachments
Note: GTAC audit does not provide guidance for level 3 and above configuration.